## Slide 1: Sustainability Principles and Practice, 4th ed.
Designing a rainwater harvesting system:
Sizing the system

## Slide 2
VectorMine, Dreamstime
To determine how much rainwater you can harvest
Find the area of your roof
Find monthly precipitation data (rainfall) for your area

## Slide 3: Find area of your roof in square feet
Area = length x width
Based on footprint
Differences in roof slope do not affect catchment area
Image courtesy of Texas A&M AgriLife Extension

## Slide 4: Find monthly precipitation data for your area
Another US source is NOAA’s National Weather Service, at https://www.weather.gov/ffc/rainresrc :
For example, these data are for Eugene, Oregon
In the US, one source is NOAA’s National Center for Environmental Information, at https://www.ncei.noaa.gov/products/land-based-station/local-climatological-data
NOAA National Weather Service

## Slide 5
Another US source, nongovernmental, is https://www.usclimatedata.com
These data are for Eugene, Oregon
Temperature:

## Slide 6: Determine how much rainwater is available for harvesting
One inch of rain on one square foot of catchment area = 0.623 gallons
Harvested = catchment x 0.623 x rainfall
water (gal) area (ft2) conversion amount
factor (in.)
One inch of rain on 1000 square feet of catchment area = 623 gallons
or

## Slide 7: Why 623 gal per inch of rain on 1000 sq ft roof?
1 sq ft = 144 sq in
1000 sq ft = 144,000 sq in
If there are 144,000 sq in. in area, 1 in. deep,
then there are 144,000 cu in. in volume.
12” x 12” = 144 sq in

## Slide 8: Why 623 gal per inch of rain on 1000 sq ft roof?
1 gallon contains 231 cubic inches
144,000 cu in
231 cu in/gal
 623 gal

## Slide 9: Water budget
Harvested = rainfall x 0.623 x catchment x 0.75
water (gal) amount conversion area (ft2)
(in.) factor
75% of annual rainfall can be stored
Rest is lost to evaporation and inefficiencies

## Slide 10
Let’s say your rainfall is similar to Eugene, Oregon:
NOAA National Weather Service

## Slide 11: Example: 30 ft x 50 ft roof
Harvested water = rainfall x 0.623 x catchment x 0.75
Water budget = 40.83 in x 0.623 x 1500 sq ft x 0.75
(annual conversion (30 x 50) (75%)
precip.) factor
Annual water budget = 28,617 gallons per year

## Slide 12: Monthly water budget
Harvested water = rainfall x 0.623 x catchment x 0.75

## Slide 13: Estimate how much water you need
Toilet flushing: 3500 gal/year per person
  A low-flow toilet uses 1.6 gal/flush
  6 flushes/person/day
  1.6 x 6 = 9.6 gal/person/day = 3500 gal/person/year
Indoor use
Tank and pipes must be marked nonpotable
Purple pipe or nonpotable marking
US Department of Public Health

## Slide 14: Estimate how much water you need
Demand depends on climate and plant type
  Evapotranspiration (ET) is an estimate of demand
  Evapotranspiration: combined loss of water from soil and leaves due to evaporation and plant transpiration (uptake and use of water)
Estimate monthly demand, if possible
  Plants will not need irrigation during rainy season
Outdoor use
Most common use for rainwater harvesting is landscape irrigation
Do not use nonpotable water on plants that are eaten
  Or, rule of thumb: on average, plants need about 1 inch of water per week
  Measure using a rain gauge or a canned-food can

## Slide 15: Example
500 sq ft vegetable garden
100 sq ft flowers
600 sq ft shrubs
Let’s say you have:
Hunter Irrigation
Total: 1200 sq ft landscape area
To find ET data, try local county extension office, state or provincial climatologist, nearby universities, or national climate data
-- outdoor use only

## Slide 16: Let’s say typical evapotranspiration data for your area is this:
Then the water you will need each month is:
ET: evapotranspiration

## Slide 17: Calculate cumulative water balance – “checkbook” method
Last month’s storage
+ this month’s yield
─ this month’s demand
= this month’s storage
If answer is a negative number, i.e., demand is greater than supply,
put it in the supplemental column. That’s how much supplemental water you will need for that month.

## Slide 18: Cumulative water balance – “checkbook” method
In winter, supply exceeds demand, so you can store and save water for summer.
In summer, you will still need some supplemental water.

## Slide 19: Cumulative water balance
The largest storage value is in February.
It shows that if you want to use all the rainfall available, you will need a tank that can store at least 10,327 gal.
  You’d need a tank larger than 10,000 gal.
(If every year were like this year.)

## Slide 20: Note:
In our example, we used National Weather Service data that gave the average precipitation for Eugene, Oregon from 1890 to 2023, and it appeared we would have collected a lot of rainwater.
However, with climate change, average precipitation is decreasing in many regions.
For example, here is Eugene’s annual precipitation from 2020 to 2023:

## Slide 21: If supply of harvested water does not meet demand, you could:
Increase catchment area
Add supplemental water, such as municipal supply
Reduce landscaped area
Reduce plant density
Use mulch to reduce evaporation
Change to plants that require less water
Increase supply:
Reduce demand: